Facilities Services COVID Shelter In Place Planning

3-17-20

Program dependencies:

- how many students remain on campus, if any

- how many faculty/staff need access to buildings

- temperatures remain moderate, need for AC will require adjustments

Critical spaces:

- Animal holding in Knapp has electric reheat and Talbot boiler can provide heat as needed after HP shut down

- IT server room is on its own unit

- Ebaugh/Talbot labs will need the Talbot boiler once HP is shut down

- Museum is fed from Eisner plant, leave Eisner in operation

- The natatorium presents some challenges without the HP since we'll still need to maintain humidity operational changes will be required.

Heating Plant:

- Run central plant as long as possible, probably at least another 2-3 weeks.  Shut down as soon as mild temperatures allow.

- Get Sam-Tal boilers reassembled and ready to operate to provide steam to A-Quad buildings.  Can maintain temperatures in buildings if outside air temp stays above ~50℉, below that, buildings will be cooler than desired.

General buildings:

- Depends on use – set back or turn off HVAC where possible

- Academic buildings scheduled to minimize energy usage – depends on usage

Res Halls:

- Set all apartments to 55°

- Once vacated, either adjust the heating reset controllers or turn them completely off depending on forecast and availability of heating plant.

- Shut off hot water once vacated

Staffing:

Assumes employees are ‘critical’

Maintain current zones under current circumstances: Trades to report to your zone, maintain social distancing if you have contact with others;  BSA’s to report to assigned building.

In the event of a 'shelter in place' order:

- send everyone home other than the heating plant

- handle all maintenance requests on a reactionary basis by zone

- Have one person from each zone walk their buildings Monday and Thursday of every week

- Potentially have HVAC techs monitor buildings from home in leu of having to walk buildings

- Trash pick up will be required as needed depending on how many people are on campus

- No services will be provided for offices or classrooms, public restrooms/building space will be policed by BSA’a or Supervisory staff on a weekly basis – depending on use

- Grounds will need to start cutting grass – details of how to do this pending

Room Clean Out:

Depends on how many rooms need just cleaned or packed and when/if ‘shelter in place’ is in effect or lifted.

- Estimated 5-8 days for BSA’s to pack rooms, additional time to relocate boxes to storage in Facilities Pole barn and Moon Hall (maybe other spaces TBD)

- Clean out of refrigerators needs to happen asap.

- Once rooms are cleaned, and ‘shelter in place’ is lifted, Trades staff can begin to address maintenance needs – reducing the need for contractor support