## Instructions
We have to | il
Shop Responsibilities
Update status/checklist daily for each building.
Enter status update in column B for the system components in each buliidng tab. There is a drop down menu for status: 1, 2, 3, and 4
Enter any notes on status in column C for the system component. If a work order is needed, submit request to the Customer Service Center.
Customer Service Center Responsibilities
Update builidng checklist with Work Order # in column. D for the appropriate system.
Use Summary Page as a reference for communication if requested from Facilities Liaisons.

## Restart Summary
Phase I: Research Building COVID-19 Restart Summary
Count | Overall Status | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House- Keeping | Sewer Line | Liaisons Notified | WO#
A-1 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068798
A-2 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068801
A-3 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068799
A-4 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068802
A-5 | YELLOW | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068805
A-6 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068807
A-7 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068808
B-1 | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | Y | 20-068809
B-2 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068810
B-3 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068800
B-4 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068811
B-5 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068812
B-6 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068813
B-7 | YELLOW | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068814
B-8 | YELLOW | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068815
B-9 | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068816
B-10 | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068817
B-11 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068818
B-12 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068821
B-13 | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068825
B-14 | YELLOW | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068824
B-15 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068828
B-16 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068826
B-17 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068827
B-18 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068829
C-1 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068984
C-2 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068990
C-3 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068991
C-4 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068992
C-5 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068993
C-6 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068996
C-7 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068997
C-8 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068999
C-9 | YELLOW | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-068818
C-10 | NC | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN |  | 20-069000
C-11 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-069006
C-12 | NC | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN |  | 20-069009
C-13 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-069010
D-1 | NC | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | NC |  | 20-071739
D-2 | NC | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | NC |  | 20-071740
D-3 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-071759
D-4 | NC | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | GREEN | NC |  | 20-071745
D-5 | NC | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | GREEN | GREEN |  | 20-071746
D-6 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | N | 20-071747
D-7 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y | 20-071752
D-8 | YELLOW | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | Y
D-9 | NC | NC | YELLOW | GREEN | GREEN | GREEN | GREEN | NC | GREEN | NC | NC | NC | GREEN | NC | GREEN |  | 20-071754
D-10 | NC | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | NC |  | 20-071755
D-11 | NC | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | GREEN | NC | GREEN | GREEN | NC | NC |  | 20-072065
D-12 | NC | NC | NC | NC | NC | GREEN | GREEN | NC | GREEN | NC | NC | NC | NC | RED | NC |  | 20-072066
D-13 | NC | NC | NC | NC | NC | GREEN | GREEN | NC | GREEN | NC | NC | GREEN | NC | GREEN | NC |  | 20-072067
D-14 | NC | NC | NC | NC | NC | GREEN | GREEN | NC | GREEN | NC | NC | NC | NC | NC | NC |  | 20-072080
Phase I: Auxilliary Building Restart Summary
Count | Overall Status | Air Handling | BA System | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Water & Sewer | Emer. Gens | Nat. Gas | House- Keeping | Sewer Line | Liaisons Notified | WO#
B-19 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN |  | GREEN | N | 20-068914
B-20 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | N | 20-068915
B-21 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | N | 20-068916
B-22 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | N | 20-068916
C-14 | NC | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN |  | 20-069011
D-15 | NC | GREEN | NC | GREEN | GREEN | GREEN | NC | NC | NC | GREEN | NC | GREEN | GREEN |  | 20-072081

## A1
A-1 | WO# | 20-068798
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] | Filter media changed 5/19/20. |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | , |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] | 6 rooms to check slightly Positive, Semens control and Denny in on 19th to correct. Work completed on 5/20/20 . | 20-068938 | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] | Test good. |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | Cummins to troubleshoot today 5/8/2020. Low prestart oil pressure alarm > Update good to go per Cummins | 20-068616 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | Natural Gas Unit |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No natural gas in building. |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## A2
A-2 | WO# | 20-068801
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] | AHU 1 Dampers need work to function properly but is causing no issues. | 20-068882 | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | The system is functional, but need a shutdown is scheduled for May 23 to make warranty repair to the steam condensate return tank. This is the steam system. | 20-036993 | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] | There is no building static control |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go]
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057611 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## A3
A-3 | WO# | 20-068799
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the low-occupancy building flush checklist. | 1 [Good to Go]
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-066800 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## A4
A-4 | WO # | 20-068802
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057671 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## A5
A-5 | WO # | 20-068805
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 2 [Minor Issue] | Three dampers are not functioning properly | 20-068886 | 2
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 4 [Not Checked] | NA |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] | NA |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] | NA |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057678 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## A6
A-6 | WO # | 20-068807
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] | N/A |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] | N/A |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | N/A |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] | N/A |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | Handled and checked by department |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | N/A |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | N/A |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | N/A |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | Building was occupied and flowing water |  | 1

## A7
A-7 | WO # | 20-068808
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057665 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | gas shut off at meter for years |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B1
B-1 | WO# | 20-068809
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | No heat recovery in this AHU |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] | Bldg does not have BAS. |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] | Bldg does not have BAS. |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | Bldg does not have BAS. |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | No vacuum system in this bldg. |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | No process chill water in bldg |  | 1
Check RO/DI water systems to ensure they are operational. |  | No ro/di water in bldg |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] | Chill water good, No towers on site |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] | Chill water good, No towers on site |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | Building does not have an elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | N/A |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 2 [Minor Issue] | Still on going,ran out of strips |  | 2
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057646 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No pilot lights in greenhouses only hot water for heat. |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B2
B-2 | WO# | 20-068810
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | N/A | No heat recovery in this bldg |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | N/A | No BAS in Bldg |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | N/A | No BAS in Bldg |  | 1
Confirm lighting control system schedule is set to normal operating times. | N/A | No BAS in Bldg |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | N/A | No vacuum system in bldg. |  | 1
Confirm the Process Chillled Water System is operational. | N/A | No Process chilled water |  | 1
Check RO/DI water systems to ensure they are operational. | N/A | No ro/di water in bldg |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] | No towers here |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | Building does not have an elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | N/A | No BAS in this bldg |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057645 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No gas in houses,just hot water |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] | NA Greenhouse, csb |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B3
B-3 | WO # | 20-068800
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | No heat recovery inbldg |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] | No BAS in bldg |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] | No BAS in bldg |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | No BAS in bldg |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | No vacuum system in bldg |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | No process chilled water |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | No ro/di water |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] | No Bas in bldg |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the low-occupancy building flush checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057642 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | N/A | No heaters in houses,only hot water |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B4
#REF! | WO# | 20-068811
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | No heat recovery in bldg |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] | No BAS in bldg |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] | No BAS in bldg |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | No BAS in bldg |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | No vacuum system in bldg |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | No processed chilled water |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | No ro/di water in bldg |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] | No BAs in bldg |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057641 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No gas heaters in houses,only hot water |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B5
#REF! | WO# | 20-068812
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | N/A done in labs |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] | 6 labs need to be checked. work completed 5/20/20 | 5 | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] | Test are good. |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057613 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No Natural gas in building. |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B6
#REF! | WO # | 20-068813
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | N/A |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-066803 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B7
#REF! | WO # | 20-068814
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | NA |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | NA |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 2 [Minor Issue] | Small leak around pump, parts are ordered and repair will need to be scheduled with the customer. This will not affect building or lab operation. |  | 2
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057651 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No pilot |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B8
#REF! | WO # | 20-068815
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 2 [Minor Issue] | manully operated, control issues |  | 2
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-058644 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B9
#REF! | WO # | 20-068816
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] | Adjustments needed | 20-068883 | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | NA |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] | Commissioning team onsite |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | NA |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | NA |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] | On campus loop. |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] | NA |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 2 [Minor Issue] | FH in G108 no flow | 20-068884 | 2
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 2 [Minor Issue] | FH in G108 no flow | 20-068884 | 2
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057638 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | April water use was 62% of normal |  | 1

## B10
#REF! | WO # | 20-068817
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | NA |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | NA |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] | Nitrate level needed increasing and already has a work order from last PM- Nitraite levels have been increased to proper levels |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 2 [Minor Issue] | Failed motor on general building exhaust, multipal motors operational, failed motor on order | #5 | 2
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057656/20-057655 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No pilots, just lab equipment |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B11
#REF! | WO # | 20-068818
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] | Work order is in for outside screen repair, but it is not impacting the building |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | NA |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | NA |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | NA |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] | Room 3101 has low flow /This issues has been repaired 5/19/20 |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] | Room 3101 was positive to the hallway /This issues has been repaired 5/19/20 |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057616 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No pilots, just lab equipment |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B12
#REF! | WO # | 20-068821
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | Note two gensets at Dabney One relocated from VRB Both have had PM's | 20-057666 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B13
#REF! | WO # | 20-068825
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | N/A |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 2 [Minor Issue] | original condition,Project in progress to correct.Control Shop is working this |  | 2
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | Two gensets at Tox | 20-057630 / 20-057629 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | Natural gas not diesel |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B14
#REF! | WO # | 20-068824
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] | Building is on Loop |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 2 [Minor Issue] | #1 elevator is out of service. Additional elevator in the building. Liaisons notified. |  | 2
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057680 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B15
#REF! | WO# | 20-068828
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] | Mostly window units |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | only 1 unit has this feature |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] | Mostly window units |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] | Mostly window units |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | Mostly window units |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. |  |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] | No chill water |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] | No chill water |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057664 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B16
#REF! | WO # | 20-068826
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | N/A | No process chilled water in this bldg |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057614 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | N/A | No pilot lights in this bldg |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B17
#REF! | WO# | 20-068827
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | N/A |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | Water softener is good |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057661 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | N/A |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | Building was occupied and flowing water |  | 1

## B18
#REF! | WO# | 20-068829
Research Building Restart Checklist | Status | Notes | WO # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] | Building is on Loop |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057624 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | April water usage at 59% of normal |  | 1

## B19
#REF! | WO # | 20-068914
Auxilliary Building Restart Checklist | Status | Notes | WO # | Code | Air Handling | BA System | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  | 1 | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057695 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. |  | Facilities does not handle housekeeping for this building.
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B20
#REF! | WO # | 20-068915
Auxilliary Building Restart Checklist | Status | Notes | WO # | Code | Air Handling | BA System | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 4 [Not Checked] | N/A |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] | Water flowed. |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] | No Generator at this building |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. |  | N/A |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] | N/A, No gas |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B21
Weisiger-Brown | WO # | 20-068916
Auxilliary Building Restart Checklist | Status | Notes | WO # | Code | Air Handling | BA System | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | NA |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | NA |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | No Elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | N/A No fire pump |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | This genset does not function. It has not been maintained by Power Systems in 5 year, A note in AIM (12/10/2015) states UNIT OUT OF ORDER, AWAITING ATHLETICS DEPARTMENT. PLACED IN "REMOVED" STATUS. The Athletic Department is good to go without emergency power backup. |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | See above |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | na |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## B22
#REF! | WO | 20-068916
Auxilliary Building Restart Checklist | Status | Notes | WO # | Code | Air Handling | BA System | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | na |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | na |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | No elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NO FIRE PUMP ENGINE |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone) |  |  |  | .
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | This building is fed from WB Building. |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | NA |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | na |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C1
#REF! | WO# | 20-068984
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] | Section A-F are good |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | AHU's 4,5,6,10 are good no leaks |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | Lights are not controlled from BAS. |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | N/A | No processed chilled water |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | N/A | Chill water testing is done by the Central plant group. |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] | Static psi is high on ahu's 7 & 15 due to the fact there is no VFD on the ahu's. |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] | Hot water comes from the plant. |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | N/A | No gas heaters in this bldg |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C2
#REF! | WO # | 20-068990
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] | Building is on Loop |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | n/a |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057631 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C3
#REF! | WO # | 20-068991
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | NA |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C4
#REF! | WO# | 20-068992
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] | Screen needs repair, but not affecting system | 6 | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | na |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] | Room 6109 fh#477 not working-Issue has been repaired and hood retested | phase 5 | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] | Check and adjust room pressurization in 6109 - 4112 - 4104 - Pressurization issues and adjustments are complete | 2009-07-08 | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | no pilots |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | Water use in April at 200% of April 2019 |  | 1

## C5
#REF! | WO# | 20-068993
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057670 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C6
#REF! | WO # | 20-068996
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057672 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C7
#REF! | WO# | 20-068997
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | NA |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | NA |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | This building has no genset |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C8
#REF! | WO# | 20-068999
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | N/A |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] | Lincoln Harris has a beam detector that needs to be removed and heat detector installed.System has one trouble. |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | 2- gensets |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | 2-gensets one diesel one NG |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C9
#REF! | WO# | 20-068818
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 2 [Minor Issue] | Outside air damper is not functioning correctly, but outside air is open and building will not be negitively affected. Work order has been issued | 5 | 2
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | NA |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | Need filters for replacement- filters replaced | 6 | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | na |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | na |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 2 [Minor Issue] | five hoods are low. - All hoods are repaired and rechecked | 007,8,9,10,11 | 2
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057616 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | No pilots |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C10
#REF! | WO# | 20-069006
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057609 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] | Staff is in the process of cleaning the building now, will take until COB Friday or early Monday. |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C11
#REF! | WO# | 20-069000
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | N/A |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C12
#REF! | WO# | 20-069009
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] |  |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 2 [Minor Issue] |  |  | 2
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | 2-gensets one had fuel dilution in oil GP changed oil and filters. Second genset needed coolant. Good to go now | 20-057668 / 20-057667 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | gas valve off outside bldg. |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] | The building is being cleaned and should be completed by Friday COB. |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C13
#REF! | WO# | 20-069010
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | na |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | na |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | na |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | na |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | Building does not have an elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | na |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] | Just for information - Only one fume hood in the building. A project was started to install a replacement hood, but was never completed. this is a deparment and an EH&S project and not a zone shop project. |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | This building has no genset |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | na |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## C14
#REF! | WO# | 20-069011
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-058603 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## D1
#REF! | WO# | 20-071739
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | , |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | NA |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | NA |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | NA |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | NA |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] | NA |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] | NA |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | 2 working gensets at this building. One for NWS. A 3rd gensrt is there it is private (Grifolls) and is not maintained, | 20-057676 / 20-067714 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | NA |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## D2
#REF! | WO# | 20-071740
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | , |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | NA |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | NA |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | NA |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | NA |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | NA |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] | NA |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] | NA |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | N/A no genset |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | N/A no genset |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | NA |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## D3
#REF! | WO# | 20-071759
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | , |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] | Photo cell |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | N/A |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] | Not on VFD |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] | N/A |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | N/A no genset |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | N/A no genset |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## D4
#REF! | WO# | 20-071745
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | GREEN | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 2 [Minor Issue] | AHU 2 damper not operating correctly | 5 | 2
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | NA |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | NA |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | NA |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] | Note* Lab 134B Is in a project to replace a hood and it is currently not in service. |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] |  |  | 4
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 4 [Not Checked] |  |  | 4
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | na |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## D5
#REF! | WO# | 20-071746
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | GREEN | GREEN | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | , |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] | N/A |  | 1
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | N/A |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] |  |  | 4
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 4 [Not Checked] |  |  | 4
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## D6
#REF! | WO# | 20-071747
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] | Dampers repaired but need replacement parts ordered to replace what was used | 2020-05-06 | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | na |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | na |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | na |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] | na |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | Building does not have an elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057644 / 20-057861 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] | NA |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | Water usage at 83% of normal |  | 1

## D7
#REF! | WO# | 20-071752
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | 1
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | , |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | N/A |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] | N/A |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | Water usage at 58% of normal |  | 1

## D8
#REF! | WO#
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | YELLOW | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | YELLOW | 2
Verify air dampers, including Outside Air Dampers, are functional. | 2 [Minor Issue] | Lingering issues because of the corrosive enviornment |  | 2
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | , |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | UD shop doesn't maintain this line. |  | 1

## D9
#REF! | WO# | 20-071754
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | NC | YELLOW | GREEN | GREEN | GREEN | GREEN | NC | GREEN | NC | NC | NC | GREEN | NC | GREEN | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 4 [Not Checked] |  |  | 4
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 2 [Minor Issue] | Some controls issues due to power outage. It is being addressed by the Control and Zone shop. |  | 2
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] | N/A |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | Building does not have an elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 4 [Not Checked] |  |  | 4
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 4 [Not Checked] |  |  | 4
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 4
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 4 [Not Checked] |  |  | 4
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] |  |  | 4
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 4 [Not Checked] |  |  | 4
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] | Water usage > 100% of normal |  | 1

## D10
#REF! | WO# | 20-071755
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | NA |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Confirm the Process Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Check RO/DI water systems to ensure they are operational. | 1 [Good to Go] |  |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 1 [Good to Go] |  |  | 1
Verify the Static Pressure Setpoint is correct. | 1 [Good to Go] |  |  | 1
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 1 [Good to Go] |  |  | 1
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  | 20-057654 | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] |  |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## D11
#REF! | WO# | 20-072065
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | GREEN | GREEN | GREEN | GREEN | GREEN | NC | GREEN | GREEN | NC | GREEN | GREEN | NC | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 1 [Good to Go] | , |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 1 [Good to Go] |  |  | 1
Confirm lighting control system schedule is set to normal operating times. | 1 [Good to Go] |  |  | 1
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 1 [Good to Go] |  |  | 1
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] | N/A |  | 1
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] | N/A |  | 1
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 1 [Good to Go] |  |  | 1
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 1 [Good to Go] |  |  | 1
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 1 [Good to Go] |  |  | 1
Complete the water quality building restart checklist. | 4 [Not Checked] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 1 [Good to Go] |  |  | 1
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | Natural gas-fired generator |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 1 [Good to Go] |  |  | 1
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## D12
#REF! | WO# | 20-072066
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | NC | NC | NC | NC | GREEN | GREEN | NC | GREEN | NC | NC | NC | NC | RED | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 4 [Not Checked] |  |  | 4
Verify Heat Recovery Equipment leakages are under control. | 4 [Not Checked] | , |  | 4
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 4 [Not Checked] |  |  | 4
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 4 [Not Checked] |  |  | 4
Confirm lighting control system schedule is set to normal operating times. | 4 [Not Checked] |  |  | 4
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] |  |  | 4
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 4 [Not Checked] |  |  | 4
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | Building does not have an elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 4 [Not Checked] |  |  | 4
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 4 [Not Checked] |  |  | 4
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 4 [Not Checked] |  |  | 4
Complete the water quality building restart checklist. | 4 [Not Checked] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 4 [Not Checked] |  |  | 4
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] |  |  | 4
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 4 [Not Checked] |  |  | 4
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] |  |  | 4
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 3 [Major Issue] | On hold for a mold issue |  | 3
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## D13
#REF! | WO# | 20-072067
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | NC | NC | NC | NC | GREEN | GREEN | NC | GREEN | NC | NC | GREEN | NC | GREEN | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 4 [Not Checked] |  |  | 4
Verify Heat Recovery Equipment leakages are under control. | 4 [Not Checked] | , |  | 4
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 4 [Not Checked] |  |  | 4
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 4 [Not Checked] |  |  | 4
Confirm lighting control system schedule is set to normal operating times. | 4 [Not Checked] |  |  | 4
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] |  |  | 4
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 4 [Not Checked] |  |  | 4
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] | Building does not have an elevator |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 4 [Not Checked] |  |  | 4
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 4 [Not Checked] |  |  | 4
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 4 [Not Checked] |  |  | 4
Complete the water quality building restart checklist. | 4 [Not Checked] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 4 [Not Checked] |  |  | 4
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] | No genset. |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | No genset. |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] |  |  | 4
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 1 [Good to Go] |  |  | 1
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## D14
#REF! | WO# | 20-072080
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | NC | NC | NC | NC | GREEN | GREEN | NC | GREEN | NC | NC | NC | NC | NC | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 4 [Not Checked] |  |  | 4
Verify Heat Recovery Equipment leakages are under control. | 4 [Not Checked] | , |  | 4
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 4 [Not Checked] |  |  | 4
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 4 [Not Checked] |  |  | 4
Confirm lighting control system schedule is set to normal operating times. | 4 [Not Checked] |  |  | 4
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] |  |  | 4
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 4 [Not Checked] |  |  | 4
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] | NA |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 1 [Good to Go] |  |  | 1
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 4 [Not Checked] |  |  | 4
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 4 [Not Checked] |  |  | 4
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 4 [Not Checked] |  |  | 4
Complete the water quality building restart checklist. | 4 [Not Checked] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 4 [Not Checked] |  |  | 4
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] |  |  | 4
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | NA, generator fueled by gas. |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] |  |  | 4
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## Sheet63
WO#
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 4 [Not Checked] |  |  | 4
Verify Heat Recovery Equipment leakages are under control. | 4 [Not Checked] | , |  | 4
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 4 [Not Checked] |  |  | 4
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 4 [Not Checked] |  |  | 4
Confirm lighting control system schedule is set to normal operating times. | 4 [Not Checked] |  |  | 4
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] |  |  | 4
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 4 [Not Checked] |  |  | 4
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 4 [Not Checked] |  |  | 4
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 4 [Not Checked] |  |  | 4
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 4 [Not Checked] |  |  | 4
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 4 [Not Checked] |  |  | 4
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 4 [Not Checked] |  |  | 4
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 4 [Not Checked] |  |  | 4
Complete the water quality building restart checklist. | 4 [Not Checked] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 4 [Not Checked] |  |  | 4
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] |  |  | 4
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 4 [Not Checked] |  |  | 4
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] |  |  | 4
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## D15 081 WSC
#REF! | WO # | 20-072081
Auxilliary Building Restart Checklist | Status | Notes | WO # | Code | Air Handling | BA System | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | GREEN | NC | GREEN | GREEN | GREEN | NC | NC | NC | GREEN | NC | NC | GREEN | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 1 [Good to Go] |  |  | 1
Verify Heat Recovery Equipment leakages are under control. | 4 [Not Checked] | N/A |  | 1
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition) | 1 [Good to Go] |  |  | 1
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 4 [Not Checked] |  |  | 4
Confirm lighting control system schedule is set to normal operating times. | 4 [Not Checked] | N/A |  | 1
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 1 [Good to Go] |  |  | 1
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 1 [Good to Go] |  |  | 1
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 1 [Good to Go] |  |  | 1
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 1 [Good to Go] |  |  | 1
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 4 [Not Checked] |  |  | 4
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 4 [Not Checked] |  |  | 4
Complete the water quality building restart checklist. | 4 [Not Checked] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 4 [Not Checked] |  |  | 4
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 1 [Good to Go] |  |  | 1
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 1 [Good to Go] | NA, generator fueled by gas. |  | 1
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] |  |  | 4
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 1 [Good to Go] |  |  | 1

## Sheet62
WO#
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 4 [Not Checked] |  |  | 4
Verify Heat Recovery Equipment leakages are under control. | 4 [Not Checked] | , |  | 4
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 4 [Not Checked] |  |  | 4
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 4 [Not Checked] |  |  | 4
Confirm lighting control system schedule is set to normal operating times. | 4 [Not Checked] |  |  | 4
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] |  |  | 4
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 4 [Not Checked] |  |  | 4
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 4 [Not Checked] |  |  | 4
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 4 [Not Checked] |  |  | 4
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 4 [Not Checked] |  |  | 4
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 4 [Not Checked] |  |  | 4
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 4 [Not Checked] |  |  | 4
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 4 [Not Checked] |  |  | 4
Complete the water quality building restart checklist. | 4 [Not Checked] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 4 [Not Checked] |  |  | 4
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] |  |  | 4
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 4 [Not Checked] |  |  | 4
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] |  |  | 4
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4

## Sheet64
WO#
Research Building Restart Checklist | Status | Notes | Phase # | Code | Air Handling | BA System | Lab Supply | CW & CTs | Elev. Shop | Fire Pump | Exhaust Systems | Fire Alarms | Fume Hoods | Water & Sewer | Emer. Gens | Nat. Gas | House-Keeping | Sewer Line | OVERALL | MAX
Air Handling System (BM&O Zone) |  |  |  |  | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | NC | 4
Verify air dampers, including Outside Air Dampers, are functional. | 4 [Not Checked] |  |  | 4
Verify Heat Recovery Equipment leakages are under control. | 4 [Not Checked] | , |  | 4
BAS Controls Section (BM&O Zone)
Review system equipment status and faults. If failing to run as commanded, resolve the issue to get operational. (Such as fan status commanded on and status off, check starter VFD for Auto and belt condition). | 4 [Not Checked] |  |  | 4
Disable Demand Control Ventilation. Verify building occupancy schedule is set to "occupied'" 2 hours prior and 2 hours after the building occupants use of the space. | 4 [Not Checked] |  |  | 4
Confirm lighting control system schedule is set to normal operating times. | 4 [Not Checked] |  |  | 4
Laboratory Supply Systems (BM&O Zone)
Change filters in the air compressor systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Change filters in the vacuum systems that have not been replaced within the timeframe recommended by the manufacturer. | 4 [Not Checked] |  |  | 4
Confirm the Process Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Check RO/DI water systems to ensure they are operational. | 4 [Not Checked] |  |  | 4
Building Chilled Water & Cooling Towers (BM&O Zone)
Confirm the Building Chillled Water System is operational. | 4 [Not Checked] |  |  | 4
Confirm or the monthly chemical check has been completed within the 30 day period prior to restart or perform one prior to restart. | 4 [Not Checked] |  |  | 4
BM&O Elevator Shop
Confirm monthly safety check has been completed within the 30 day period prior to restart. If not, then perform a safety check prior to restart. | 4 [Not Checked] |  |  | 4
Fire Pump Engines (BM&O Zone)
Confirm or the monthly readiness check on fire pump engines has been completed within the 30 day period prior to restart. If not, then perform one prior to restart. | 4 [Not Checked] |  |  | 4
Exhaust Systems (BM&O Zone)
Verify the exhaust system is functional and air is flowing in the correct direction. | 4 [Not Checked] |  |  | 4
Verify the Static Pressure Setpoint is correct. | 4 [Not Checked] |  |  | 4
BM&O Electronics Shop
Confirm a readiness check has been completed for the fire alarms within the 90 day period prior to restart. If not, check fire alarms prior to restart. | 4 [Not Checked] |  |  | 4
Fume Hoods (BM&O Zone)
Verify fume hoods are operational. | 4 [Not Checked] |  |  | 4
Check the room pressurization in each individual lab to verify they are correct (i.e. positive or negative). | 4 [Not Checked] |  |  | 4
Water and Sewer (BM&O Zone)
Refill plumbing traps(not on automatic primers) with water preferably prior to performing the final building flush. | 4 [Not Checked] |  |  | 4
Complete the water quality building restart checklist. | 4 [Not Checked] |  |  | 4
Verify all water heaters and hot water storage tanks (if any) are set at the normal operation temperature. | 4 [Not Checked] |  |  | 4
Utilities Power Systems
Confirm the monthly readiness check for generators has been completed within the 30 day period prior to restart. If not, then perform a readiness check prior to restart. | 4 [Not Checked] |  |  | 4
Refill fuel storage tank if fuel volume is not at 5/8th's or more of capacity. | 4 [Not Checked] |  |  | 4
Natural Gas (BM&O Zone)
Verify the natural gas pilot light is on and appears to have sufficient air flow for the appliances that burn natural gas. | 4 [Not Checked] |  |  | 4
Housekeeping
Perform a thorough cleaning of the building. Pay particular attention to cleaning and disinfecting frequently touched surfaces such as door handles, stairway railings, elevator buttons, reception desks, push plates, light switches and faucet handles. | 4 [Not Checked] |  |  | 4
Sewer Line (UD Shop)
Flush the sewer line. | 4 [Not Checked] |  |  | 4